## Tabelle1
UID | Building | Type | Details | Sensor | Unit | Resolution | Calibration
temp_amb | Backbone Roof | Air temp. | Ambient air temperature, | Thies Clima WSC 11 | °C | 0.15 | No
Type: PT1000
Range: -30…+60°C
Accuracy: +-1°C @ wind speed 2m/s and between -5…+25°C
measured on NEST's rooftop.
irrad | Backbone Roof | Radiation | Global irradiation measured on NEST's rooftop | Thies Clima WSC 11 | W/m2 | 1 | No
Accuracy: +-10%
Spectral range: 350...1100 nm
heating_power | UMAR | Heating power | Power supplied to the ceiling heating of the whole building. | Belimo | kW | 0.01 | NA
EV015R+BAC
cooling_power | UMAR | Cooling power | Power supplied to the ceiling cooling of the whole building. | Belimo | kW | 0.01 | NA
EV015R+BAC
y1_272, y1_273, y2_273, y3_273, y1_274, y1_275, y1_276 | UMAR | Valve position | One valve each for rooms 272, 274, 275 and 276, and three valves for room 273 are monitored. | Afrisco TSA-02 | Open/ closed | bool | NA
window_272, window_273_1, window_273_2, window_274 | UMAR | Window state | The position of windows is assessed in rooms 272, 273 (2x) and 274. The windows are either closed or not-closed, labled as "open". The degree of window openings is not assessed. | DEFA 900103B | Open/ closed | bool | NA
temp_272, temp_273, temp_274, temp_275, temp_276 | UMAR | Air temp. | Indoor room temperatures are measured in rooms 272 – 276. | alphaEos SENSE | °C | 0.1 | NA
setp_272, setp_273, setp_274, setp_275, setp_276 | UMAR | Heating/cooling set point | Heating and cooling set points for each room 272 – 276. | Viega | °C | 0.5 | NA
Fonterra Smart Control
dhw_power | UMAR | Hot water | Charging power of the domestic hot water tank. | Neovac | kW | 0.1 | MID
Superstatic
dhw_volume | UMAR | Hot water storage | Water consumption via a fresh water station heated by the domestic hot water tank. | Neovac | l/min | 0.1 | MID
WMTWS-M
total_active_power | UMAR | Electricity | Total electricity consumption. | Beckhoff | kW | 0.1 | NA
EL EL3443
y1_living, | SolAce | Valve position | One valve for the office and one valve for the meeting space is monitored. | Honeywell | % | 0.1 | NA
y1_office
blinds_height_F1, | SolAce | Blinds | Blind positions in the office (F1 & F2) and the meeting space (F3 & F4). At 100%, blinds are fully closed. The office space has slat blinds (14m2), the meeting space fabric blinds (6.4m2). | Griesser | % | 1 | NA
blinds_height_F2, |  |  |  | FMX-IH
blinds_height_F3,
blinds_height_F4
temp_meeting, | SolAce | Air temp. | Indoor room temperatures are measured in the meeting and in the office space. | ABB LGS/A 1.2 | °C | 0.1 | NA
temp_office
setp_meeting, | SolAce | Heating/cooling set point | One temperature setpoint is monitored for the office and the meeting space. | ABB LGS/A 1.2 | °C | 0.1 | NA
setp_office
heating_power | SolAce | Heating power | Power supplied to the ceiling heating of the whole building. | NeoVac | kW | 0.01 | MID
Superstatic 749
cooling_power | SolAce | Cooling power | Power supplied to the ceiling cooling of the whole building. | NeoVac | kW | 0.01 | MID
Superstatic 749
pv_active_power | SolAce | Photovol. | PV electric active power. | ABB | kW | 0.1 | NA
Trio UNO-DM-3.3
total_active_power | SolAce | Electricity | Total electric active power (includes pv_active_power). | Beckhoff | kW | 0.1 | NA
EL EL3443
presence_meeting, presence_office | SolAce | Presence | IR Presence detection in the meeting and office space. Detects also sitting activities. | ABB | 0/1 | bool | NA
6131/31-24-500
temp_371, temp_472, temp_474, temp_476, temp_571, temp_573, temp_574 | DFAB | Air temp. | Indoor room temperatures are measured in all rooms (371 – 574). | Viega | °C | 0.5 | NA
Fonterra Smart Control
setp_371, setp_472, setp_474, setp_476, setp_571, setp_573, setp_574 | DFAB | Heating/cooling set point | One temperature setpoint for each room (371 – 574). | Viega | °C | 0.5 | NA
Fonterra Smart Control
y1_371, y2_371, y3_371, y4_371, y5_371, y6_371, y7_371, y1_472, y2_472, y3_472, y1_474, y1_476, y2_476, y3_476, y1_571, y2_571, y3_571, y1_573, y1_574, y2_574, y3_574 | DFAB | Valve position | One valve for each heating/cooling circuit in all rooms (371 – 574). | Viega | Open/ closed | bool | NA
Fonterra Smart Control
heating_cooling_power | DFAB | Heating/cooling power | Power supplied to the floor heating/cooling of the whole building. | NeoVac | kW | 0.01 | MID
Superstatic 749
kitchen_active_power | DFAB | Electricity | Kitchen electric active power. | ABB | kW | 0.01 | NA
CMS-700
total_active_power | DFAB | Electricity | Total electric active power. | Beckhoff | kW | 0.01 | NA
EL EL3443
shower_471, shower_571 | DFAB | Hot water | Hot water consumption of two showers. | Ifm | l/min | 0.1 | NA
SM6100